## FieldCheck Import
project_name | checklist_name | section | item_text | notes | tags
Riverside Medical Center - BAS Commissioning | AHU-1 Checkout | Fan | Verify supply fan command | Command SF from BAS at 0, 50, and 100%; confirm VFD follows. | AHU-1; BAS; Fan
Riverside Medical Center - BAS Commissioning | AHU-1 Checkout | Fan | Verify supply fan status | Confirm proof/status follows command; no false proof at 0%. | AHU-1; Status
Riverside Medical Center - BAS Commissioning | AHU-1 Checkout | Fan | Verify return fan tracking | RF tracks SF per sequence; verify the tracking offset. | AHU-1; Fan
Riverside Medical Center - BAS Commissioning | AHU-1 Checkout | Fan | Verify VFD fault feedback | Trip the VFD; confirm BAS alarm and fan-fail status. | AHU-1; VFD; Safety
Riverside Medical Center - BAS Commissioning | AHU-1 Checkout | Sensors | Verify SAT sensor | Compare BAS supply-air temp to a calibrated field meter (+/- 1F). | AHU-1; Sensor; Calibration
Riverside Medical Center - BAS Commissioning | AHU-1 Checkout | Sensors | Verify MAT sensor | Compare mixed-air temp to field reading. | AHU-1; Sensor
Riverside Medical Center - BAS Commissioning | AHU-1 Checkout | Sensors | Verify return air temp and humidity | Check RAT and RH against a field instrument. | AHU-1; Sensor
Riverside Medical Center - BAS Commissioning | AHU-1 Checkout | Sensors | Verify duct static pressure | Confirm DSP transmitter zero and span; compare to manometer. | AHU-1; Sensor; Calibration
Riverside Medical Center - BAS Commissioning | AHU-1 Checkout | Dampers | Verify OA damper stroke | Command 0-100%; confirm full stroke and end switches. | AHU-1; Damper
Riverside Medical Center - BAS Commissioning | AHU-1 Checkout | Dampers | Verify economizer minimum position | Confirm minimum OA position during occupied mode. | AHU-1; Damper; Economizer
Riverside Medical Center - BAS Commissioning | AHU-1 Checkout | Dampers | Verify RA/EA damper interlock | OA opens as RA closes; check linkage and travel. | AHU-1; Damper
Riverside Medical Center - BAS Commissioning | AHU-1 Checkout | Valves | Verify cooling coil valve stroke | Command CHW valve 0-100%; confirm actuator stroke. | AHU-1; Valve
Riverside Medical Center - BAS Commissioning | AHU-1 Checkout | Valves | Verify heating coil valve stroke | Command HHW valve 0-100%; confirm actuator stroke. | AHU-1; Valve
Riverside Medical Center - BAS Commissioning | AHU-1 Checkout | Safeties | Verify low-limit freezestat | Test freezestat; confirm it stops the fan and opens the HHW valve. | AHU-1; Safety; High Priority
Riverside Medical Center - BAS Commissioning | AHU-1 Checkout | Safeties | Verify smoke detector shutdown | Activate duct smoke detector; confirm fan shutdown and alarm. | AHU-1; Safety; High Priority
Riverside Medical Center - BAS Commissioning | AHU-1 Checkout | Safeties | Verify high static cutout | Confirm the high duct-static safety trips the fan. | AHU-1; Safety
Riverside Medical Center - BAS Commissioning | VAV Boxes - Floor 3 | Airflow | Verify VAV minimum airflow | Confirm minimum CFM at zero load matches the schedule. | VAV; Airflow; Floor 3
Riverside Medical Center - BAS Commissioning | VAV Boxes - Floor 3 | Airflow | Verify VAV maximum airflow | Confirm maximum CFM on a call for cooling. | VAV; Airflow; Floor 3
Riverside Medical Center - BAS Commissioning | VAV Boxes - Floor 3 | Airflow | Verify airflow sensor calibration | Check K-factor / velocity pressure against the balancer reading. | VAV; Calibration
Riverside Medical Center - BAS Commissioning | VAV Boxes - Floor 3 | Reheat | Verify reheat valve stroke | Command HHW reheat 0-100%; confirm discharge-air temp rise. | VAV; Valve; Reheat
Riverside Medical Center - BAS Commissioning | VAV Boxes - Floor 3 | Reheat | Verify discharge air temp sensor | Compare DAT to a field reading. | VAV; Sensor
Riverside Medical Center - BAS Commissioning | VAV Boxes - Floor 3 | Control | Verify zone temp sensor | Compare space temp to a field thermometer. | VAV; Sensor
Riverside Medical Center - BAS Commissioning | VAV Boxes - Floor 3 | Control | Verify occupancy override | Press the override; confirm timed occupied mode. | VAV; Occupancy
Riverside Medical Center - BAS Commissioning | Graphics Review | Navigation | Verify AHU graphic links | Confirm the graphic opens the correct equipment view. | Graphics; AHU-1
Riverside Medical Center - BAS Commissioning | Graphics Review | Navigation | Verify floor plan navigation | Confirm the floor plan links to each VAV box. | Graphics; Navigation
Riverside Medical Center - BAS Commissioning | Graphics Review | Trends | Verify SAT trend logging | Confirm SAT history is collecting at a 5-minute interval. | Graphics; Trend
Riverside Medical Center - BAS Commissioning | Graphics Review | Trends | Verify runtime totalization | Confirm fan runtime is accumulating. | Graphics; Trend
Riverside Medical Center - BAS Commissioning | Graphics Review | Alarms | Verify alarm console link | Confirm the alarm console opens and filters by AHU. | Graphics; Alarm
Riverside Medical Center - Integration & Network | BACnet Integration | Network | Verify BBMD configuration | Confirm BBMD/BDT entries are correct across subnets. | BACnet; Network; Niagara
Riverside Medical Center - Integration & Network | BACnet Integration | Network | Verify device discovery | All controllers discovered; no duplicate device instance IDs. | BACnet; Network
Riverside Medical Center - Integration & Network | BACnet Integration | Network | Verify COV subscriptions | Confirm COV is active for key points; no polling fallback. | BACnet; Network
Riverside Medical Center - Integration & Network | BACnet Integration | Points | Verify point mapping | Spot-check 10% of points map to the correct objects. | BACnet; Points
Riverside Medical Center - Integration & Network | BACnet Integration | Points | Verify units and scaling | Confirm engineering units and scaling are correct. | BACnet; Points; Calibration
Riverside Medical Center - Integration & Network | Alarm Testing | Critical Alarms | Verify space temp high/low alarm | Force an out-of-range value; confirm alarm and priority. | Alarm; High Priority
Riverside Medical Center - Integration & Network | Alarm Testing | Critical Alarms | Verify equipment fail alarm | Simulate a fan failure; confirm a critical alarm. | Alarm; High Priority
Riverside Medical Center - Integration & Network | Alarm Testing | Notifications | Verify email notification routing | Confirm alarm emails reach the on-call group. | Alarm; Notification
Riverside Medical Center - Integration & Network | Alarm Testing | Notifications | Verify alarm acknowledgment | Acknowledge an alarm; confirm state change and audit entry. | Alarm